## Instrument Sign Off
| INSTRUMENT SIGN-OFF | [8 empty] | The "Signal Working?" column refers to the program portion of the signal. For example, if a device in the field doesn't work, but we can simulate that signal with a jumper wire or read a signal via multimeter, then the Signal portion of the device would be in a good condition while the Device wouldn't.
DEVICE | SIGNAL TYPE | SIGNAL WORKING? | DEVICE WORKING? | SCADA WORKING? | UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | DEVICE MANUFACTURER | DEVICE MODEL # | COMMENTS
ESR Monitor | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Field Emergency 1 | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Field Emergency 2 | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Field Emergency 3 | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Field Emergency 4 | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Power Failure | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 OverPSI Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 1 Strip Empty Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Work Tank 2 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Cylinder 1 Liquid Level Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Work Tank 1 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Cylinder 1 Full Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 1 Door 1 Lever Closed Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Low Air Pressure | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10 |  |  | Trips at 45ish PSI. Returns at 80-85 PSI.
Water 1 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Work Tank 3 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Water 2 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Work Tank 6 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Cylinder 1 Almost Full Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Power Failure 2 | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 OverPSI Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Cylinder 2 Almost Full Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Cylinder 2 Full Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Cylinder 2 Door 1 Lever Closed Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Strip Empty Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Liquid Level Switch | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Pit 3 Level Control (Treat2 Door Pit) | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Pit 4 Level Control (Tank Farm Pit) | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Work Tank 4 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Work Tank 5 Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
Pit 2 Level Control (Treat1 Door Pit) | DI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Wax Overflow Switch | DI | Yes | Unknown | Yes | Spencer Rizer | Logan Moore | 2026-06-12 |  |  | Unable to test. Will have the same functionality that system had before.
ESD Reset | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Field Horn 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve V1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix1 M7 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Transfer Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Transfer Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Moldac Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
MCA Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix1 M4 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Door Pit Sump Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 1 Strip Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Vacuum Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Vacuum Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Door Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Tank Valve V6 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve R6 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
MCA Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve C2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
MCA Recirc Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve C3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix1 M7-3 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix1 M7-4 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
CWM Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Well Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Mix1 M4-3A Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix1 M4-4A Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 2 Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Pressure Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Pressure Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Transfer Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Strip Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Vacuum Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Seal Water Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Door Pit Sump Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Door Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Valve T1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve P1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve P2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve S1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve S2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 Valve M1-3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 Valve M4-4B | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 Valve M1-4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve V1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve SV4 | DO | Yes | No | Yes | Spencer Rizer | Logan Moore | 2026-06-10 |  |  | Signal hitting solenoid. Valve not actuating
Valve SV5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Tank Valve V4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Tank Valve V5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Seal Water Valve 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Seal Water Valve 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Wax Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Mix 3 Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M3-3 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M2-3 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve R5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve R4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Tank Farm Sump Pump | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 2 Transfer Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS6 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve SV10 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Mix 1 Valve M2-4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T6 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 Valve M4-3B | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD6 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve S3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 2 Valve T7 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve SV9 (SV8 When output off) | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Cylinder 1 Pressure Pump 1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Pressure Pump 2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve P2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve P1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve P4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve P3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve T3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve T2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve T1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve T4 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve S1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve S2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve T5 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M2-2 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M7-2 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M4-2 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Mix 1 M3-2 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve R1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Tank Valve V1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve R2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Tank Valve V2 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Valve R3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MD3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Valve MS3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Tank Valve V3 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Water 1 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Water 2 Valve | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Mix 1 Valve M1-1 | DO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Cylinder 1 Pressure Transmitter | AI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
Work Tank 6 Level Transmitter | AI | Yes | NEED TO VERIFY AT LOWER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Work Tank 1 Level Transmitter | AI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Water 1 Level Transmitter | AI | Yes | NEED TO VERIFY AT LOWER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Work Tank 2 Level Transmitter | AI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Water 2 Level Transmitter | AI | Yes | NEED TO VERIFY AT LOWER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
MCA Level Transmitter | AI | Yes | NEED TO VERIFY AT LOWER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Work Tank 3 Level Transmitter | AI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Cylinder 2 Pressure Transmitter | AI | Yes | NEED TO VERIFY AT HIGHER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Work Tank 4 Level Transmitter | AI | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Work Tank 5 Level Transmitter | AI | Yes | NEED TO VERIFY AT LOWER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Wax Level Transmitter | AI | Yes | NEED TO VERIFY AT HIGHER LEVELS | Yes | Spencer Rizer | Logan Moore | 2026-06-11
Treat1 Control Valve | AO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Treat2 Control Valve | AO | Yes | Partially | Yes | Spencer Rizer | Logan Moore | 2026-06-09 |  |  | Needs calibrated in field
Treat1 Pressure Pump Speed Command | AO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
Treat2 Pressure Pump Speed Command | AO | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-09
MCA 1 Flow Transmitter | COUNTER | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
MCA 2 Flow Transmitter | COUNTER | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
MOLDAC Flow Transmitter | COUNTER | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
CWM Flow Transmitter | COUNTER | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10
WAX Flow Transmitter | COUNTER | Yes | Yes | Yes | Spencer Rizer | Logan Moore | 2026-06-10

## Interlock Sign Off
INTERLOCK SIGN-OFF
| UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | COMMENTS
Mix1 Interlocks:
Emergency Stop | Spencer Rizer | Logan Moore | 2026-06-11
Tank Invalid (< 1) | Spencer Rizer | Logan Moore | 2026-06-12
Mix No Flow | Spencer Rizer | Logan Moore | 2026-06-12
Power Fail | Spencer Rizer | Logan Moore | 2026-06-11
Mix 1 Manual | Spencer Rizer | Logan Moore | 2026-06-12
Treat1 Using Same Work Tank, and Treat 1 Running | Spencer Rizer | Logan Moore | 2026-06-11
Treat2 Using Same Work Tank, and Treat 2 Running | Spencer Rizer | Logan Moore | 2026-06-12
SCADA & PLC Tank Different | Spencer Rizer | Logan Moore | 2026-06-12
Low Flow Rate | Spencer Rizer | Logan Moore | 2026-06-11
Selected Tank High | Spencer Rizer | Logan Moore | 2026-06-11
Mix Overtime | Spencer Rizer | Logan Moore | 2026-06-12
Low Air Pressure | Spencer Rizer | Logan Moore | 2026-06-12
Any Work Tank Overflow Switch | Spencer Rizer | Logan Moore | 2026-06-12
RIO Panel Comm Loss | Spencer Rizer | Logan Moore | 2026-06-12
Cylinder1 Interlocks:
Treat1Work Tank = Mix1 Tank while Mix1 Running | Spencer Rizer | Logan Moore | 2026-06-11
Emergency Stop | Spencer Rizer | Logan Moore | 2026-06-11
Tank Volume Less Than Required To Treat Before Running | Spencer Rizer | Logan Moore | 2026-06-12
Treat1 Door1 Open | Spencer Rizer | Logan Moore | 2026-06-11
Selected Tank Low Alarm | Spencer Rizer | Logan Moore | 2026-06-11
Low Air Pressure | Spencer Rizer | Logan Moore | 2026-06-12
VFD Fault | Spencer Rizer | Logan Moore | 2026-06-12
Treat Overtime | Spencer Rizer | Logan Moore | 2026-06-12
Power Fail | Spencer Rizer | Logan Moore | 2026-06-11
Treat2 Running With Same Work Tank as Treat 1 | CANNOT TEST | CANNOT TEST | CANNOT TEST | Reserved incase of future tank re-assignment
Treat1 OverPSI | Spencer Rizer | Logan Moore | 2026-06-11
Treat1 Tally Cubic Feet = 0 or less | Spencer Rizer | Logan Moore | 2026-06-11
Treat1 Manual | Spencer Rizer | Logan Moore | 2026-06-11
Tank Invalid (< 1) | Spencer Rizer | Logan Moore | 2026-06-11
RIO Panel Comm Loss | Spencer Rizer | Logan Moore | 2026-06-12
Both Transfer Pumps Disabled | Spencer Rizer | Logan Moore | 2026-06-12
Both Pressure Pumps Disabled
Cylinder2 Interlocks:
Treat2Work Tank = Mix1 Tank while Mix1 Running | Spencer Rizer | Logan Moore | 2026-06-12
Emergency Stop | Spencer Rizer | Logan Moore | 2026-06-12
Tank Volume Less Than Required To Treat Before Running | Spencer Rizer | Logan Moore | 2026-06-12
Treat2 Door1 Open | Spencer Rizer | Logan Moore | 2026-06-12
Selected Tank Low Alarm | Spencer Rizer | Logan Moore | 2026-06-12
Low Air Pressure | Spencer Rizer | Logan Moore | 2026-06-12
Treat Overtime | Spencer Rizer | Logan Moore | 2026-06-12
Power Fail | Spencer Rizer | Logan Moore | 2026-06-12
Treat1 Running With Same Work Tank as Treat 2 | CANNOT TEST | CANNOT TEST | CANNOT TEST | Reserved incase of future tank re-assignment
Treat2 OverPSI | Spencer Rizer | Logan Moore | 2026-06-12
Treat2 Tally Cubic Feet = 0 or less | Spencer Rizer | Logan Moore | 2026-06-12
Treat2 Manual | Spencer Rizer | Logan Moore | 2026-06-12
Tank Invalid (< 1) | Spencer Rizer | Logan Moore | 2026-06-12
RIO Panel Comm Loss | Spencer Rizer | Logan Moore | 2026-06-12
Both Transfer Pumps Disabled | Spencer Rizer | Logan Moore | 2026-06-12
Both Pressure Pumps Disabled | Spencer Rizer | Logan Moore | 2026-06-12

## Treat Sequence Sign Off
TREAT SEQUENCE SIGN-OFF
| UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | COMMENTS
STEP 1 - Initial Vacuum
Open V1, R1/2/3 and selected Tank Valve (TnKv4/TnKv5/TnKv6). | Spencer Rizer | Logan Moore | 2026-06-11
Start vacuum pumps after 3 second delay. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI setpoint | Spencer Rizer | Logan Moore | 2026-06-11
STEP 2 - Fill
Previous-step valves remain open. | Spencer Rizer | Logan Moore | 2026-06-11
Vacuum pump remains on and Control Valve holds vacuum. | Spencer Rizer | Logan Moore | 2026-06-11
Open transfer valves T1, T2, T3, T4 | Spencer Rizer | Logan Moore | 2026-06-11
After 10 seconds, Close T3, T4 valves. | Spencer Rizer | Logan Moore | 2026-06-11
When Almost Full Sensor activates: Control Valve opens 100%, vacuum pumps stops, and after 2 seconds, V1, T1 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Open T2, T4, P1, P2, P3, P4 valves. | Spencer Rizer | Logan Moore | 2026-06-11
After 6 seconds, Transfer Pump 1, Pressure Pumps 1 and 2 turn on. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI > 5 and Full sensor for 5 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 3 - Raise Pressure
Control Valve ramps down to zero, and closes. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 4 - Pressure
Transfer Pump 1 turns off. | Spencer Rizer | Logan Moore | 2026-06-11
All other valves remain open. Pressure Pumps remain running. After 2 seconds, T2, T4 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Pressure pumps continue until max PSI setpoint is reached. Once reached, the non-selected Pressure Pump turns off. After 3 seconds, non-selected Pressure Pump valves close. | Spencer Rizer | Logan Moore | 2026-06-12
Selected pressure pump continues to run and maintains PSI setpoint based on Frequency. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on injection or time. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 5 - Pressure Relief
Remaining/both pressure pump(s) shut down, and after 3 seconds, P1, P2, P3, P4 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Control Valve ramps pressure down according to cycle settings. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 6 - Empty
Control Valve opens 100%. | Spencer Rizer | Logan Moore | 2026-06-11
Once cylinder reaches 3 PSI, T1, T3 valves open. | Spencer Rizer | Logan Moore | 2026-06-11
After 7 seconds, Transfer Pump 1 turns on. After another 5 seconds, Transfer Pump 2 turns on. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system begins. From the beginning of the step, after 60 seconds of the Empty sensor showing liquid, S1, S2/3 valves open. After 5 seconds, Strip Pump turns on. | Spencer Rizer | Logan Moore | 2026-06-11
After 10 seconds of the liquid sensor showing no liquid, Transfer Pump 2 turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If liquid sensor shows liquid, Transfer pump 2 turns back on. | Spencer Rizer | Logan Moore | 2026-06-11
After 5 seconds of the Empty sensor showing no liquid, Transfer Pump 1 turns off. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on Empty sensor showing no liquid for 5 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 7 - Final Vacuum
Both transfer pumps turn off, if not off already. After 5 seconds, T1 (and T3 if strip system isn't running) valve closes. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Control valve closes completely. | Spencer Rizer | Logan Moore | 2026-06-11
V1 valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
After 5 seconds Vacuum Pumps turns on. | Spencer Rizer | Logan Moore | 2026-06-11
If PSI setpoint is reached, Vacuum Pumps turns off. Vacuum Pumps will turn back on if setpoint plus 2 PSI is reached. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on selected recipe. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 8 - Final Empty
Vacuum pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
Control Valve opens 100%. | Spencer Rizer | Logan Moore | 2026-06-11
After 2 seconds, V1 valve closes. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on Empty sensor showing no liquid, and between -1 and +1 PSI for 3 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 9 - Finish
System continues running. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on time setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
FULL CYLINDER CHECKS
Uninterrupted Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 3 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 4 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 5 | Spencer Rizer | Logan Moore | 2026-06-12
Alarm Shutdown Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-11
Alarm Shutdown Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-12
CYLINDER 2 TREAT SEQUENCE
STEP 1 - Initial Vacuum
Open V1, C2 and selected Tank Valve (TnKv4/TnKv5/TnKv6). | Spencer Rizer | Logan Moore | 2026-06-11
Start vacuum pump and seal water system after 3 second delay. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI setpoint | Spencer Rizer | Logan Moore | 2026-06-11
STEP 2 - Fill
Previous-step valves remain open. | Spencer Rizer | Logan Moore | 2026-06-11
Vacuum pump remains on and Control Valve holds vacuum. | Spencer Rizer | Logan Moore | 2026-06-11
Open transfer valves T1, T3, T4, T2 and T5/6 based on selected work tank. | Spencer Rizer | Logan Moore | 2026-06-11
After 10 seconds, Close T4, T2 valves. | Spencer Rizer | Logan Moore | 2026-06-11
When Almost Full Sensor activates: C2 closes, Control Valve opens 100%, vacuum pump stops, and V1, T1 closes. | Spencer Rizer | Logan Moore | 2026-06-11
Open C1/3, T2, P1, P2 valves, and selected R valve. | Spencer Rizer | Logan Moore | 2026-06-11
After 6 seconds, Transfer Pump 1, Pressure Pumps 1 and 2 turn on. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI > 5 and Full sensor for 5 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 3 - Raise Pressure
Control Valve ramps down to zero, and closes. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on PSI setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 4 - Pressure
Transfer Pump 1 turns off. | Spencer Rizer | Logan Moore | 2026-06-11
All other valves remain open. Pressure Pumps remain running. After 2 seconds, T2 valve closes. | Spencer Rizer | Logan Moore | 2026-06-11
Pressure pumps continue until max PSI setpoint is reached. Once reached, the non-selected Pressure Pump turns off. After 3 seconds, non-selected Pressure Pump valves close. | Spencer Rizer | Logan Moore | 2026-06-12
Selected pressure pump continues to run, and the control valve maintains PSI setpoint. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on injection or time. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 5 - Pressure Relief
Remaining/both pressure pump(s) shut down, and after 3 seconds, P1, P2, T3, T5/6 close. | Spencer Rizer | Logan Moore | 2026-06-11
Control Valve ramps pressure down according to cycle settings. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on PSI setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 6 - Empty
Control Valve opens 100%. | Spencer Rizer | Logan Moore | 2026-06-11
Once cylinder reaches 3 PSI, C1/3, R4/5/6 valves close. C2, T1, T4, T5/6 valves open. | Spencer Rizer | Logan Moore | 2026-06-11
After 7 seconds, Transfer Pump 1 turns on. After another 5 seconds, Transfer Pump 2 turns on. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system begins. From the beginning of the step, after 60 seconds of the Empty sensor showing liquid, S1, S2/3 valves open. After 5 seconds, Strip Pump turns on. | Spencer Rizer | Logan Moore | 2026-06-11
After 10 seconds of the liquid sensor showing no liquid, Transfer Pump 2 turns off. | Spencer Rizer | Logan Moore | 2026-06-11 | Unable to check due to Empty sensor losing liquid before strip empty sensor
If liquid sensor shows liquid, Transfer pump 2 turns back on. | Spencer Rizer | Logan Moore | 2026-06-11 | Unable to check due to Empty sensor losing liquid before strip empty sensor
After 5 seconds of the Empty sensor showing no liquid, Transfer Pump 1 turns off. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on Empty sensor showing no liquid for 5 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 7 - Final Vacuum
Both transfer pumps turn off, if not off already. After 5 seconds, T1, T4, T5/6 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Control valve closes completely. | Spencer Rizer | Logan Moore | 2026-06-11
V1 valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
After 5 seconds Seal Water valves open. Seal Water pump turns on. After 2 seconds, Vacuum Pump turns on. | Spencer Rizer | Logan Moore | 2026-06-11
If PSI setpoint is reached, Vacuum Pump turns off. Vacuum Pump will turn back on if setpoint plus 2 PSI is reached. | Spencer Rizer | Logan Moore | 2026-06-12
System steps on selected recipe. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 8 - Final Empty
Vacuum pump, Seal Water pump both turn off. Seal Water valves close. | Spencer Rizer | Logan Moore | 2026-06-11
Control Valve opens 100%. | Spencer Rizer | Logan Moore | 2026-06-11
After 2 seconds, V1 valve closes. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on Empty sensor showing no liquid, and between -1 and +1 PSI for 3 seconds. | Spencer Rizer | Logan Moore | 2026-06-11
STEP 9 - Finish
System continues running. | Spencer Rizer | Logan Moore | 2026-06-11
Strip system continues running. If empty sensor shows liquid for 60 seconds, S1, S2/3 valves open. After 5 seconds, Strip pump turns on. If empty sensor shows no liquid for 15 seconds, strip pump turns off. After 3 seconds, S1, S2/3 valves close. | Spencer Rizer | Logan Moore | 2026-06-11
System steps on time setpoint. | Spencer Rizer | Logan Moore | 2026-06-11
FULL CYLINDER CHECKS
Uninterrupted Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 3 | Spencer Rizer | Logan Moore | 2026-06-12
Uninterrupted Sequence 4 | Spencer Rizer | Logan Moore | 2026-06-12
Uninterrupted Sequence 5 | Spencer Rizer | Logan Moore | 2026-06-12
Alarm Shutdown Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-12
Alarm Shutdown Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-12

## Mix Sequence Sign Off
MIX SEQUENCE SIGN-OFF
| UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | COMMENTS
MIX 1 SEQUENCE
MD1/2/3/4/5/6 Valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
M1-1/M1-3/M1-4 Water valve opens 1 second after MD Valve, depending on mix system | Spencer Rizer | Logan Moore | 2026-06-11
Mix Pump 1/3/4 turns on 5 seconds after M1-1/M1-3/M1-4 Water valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
If MCA is requested, M2-2/M2-3/M2-4 opens, depending on the tank mixing | Spencer Rizer | Logan Moore | 2026-06-11
If MCA is requested, the MCA Pump turns on 3 seconds after the MCA valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
If MCA is requested & required amount is added, the appropriate MCA Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If MCA is requested & required amount is added, the MCA valve closes 1 second after MCA Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If Mold AC is requested,the M4 & M4-2/M4-3A&M4-3B/M4-4A&M4-4B valves open, depending on the tank mixing | Spencer Rizer | Logan Moore | 2026-06-11
If Mold AC is requested, Mold AC Pump turns on 3 seconds after Mold AC valves open | Spencer Rizer | Logan Moore | 2026-06-11
If Mold AC is requested & required amount is added, Mold AC Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If Mold AC is requested & required amount is added, the Mold AC valves close 1 second after Mold AC Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If CWM is requested, the M7&M7-2/M7-3/M7-4 valves open | Spencer Rizer | Logan Moore | 2026-06-11
If CWM is requested, CWM Pump turns on 3 seconds after the CWM valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
If CWM is requested & required amount is added, CWM Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If CWM is requested & required amount is added, the CWM valves close 1 second after CWM Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If WAX is requested, the M3-2/M3-3 valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
If WAX is requested, WAX Pump turns on 3 seconds after the WAX valve opens. | Spencer Rizer | Logan Moore | 2026-06-11
If WAX is requested & required amount is added, WAX Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
If WAX is requested & required amount is added, the M3-2/M3-3 valve closes 1 second after WAX Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
When required water intake is met, the Mix Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
When required water intake is met, WT Valve, M11 valves close 3 seconds after Mix Pump turns off. | Spencer Rizer | Logan Moore | 2026-06-11
IF the water required is added before a chemical finishes, the water tank valve will shut off and the tank's MS valve will open | Spencer Rizer | Logan Moore | 2026-06-11
The mix pump will circulate solution through the MS and MD valves until the required chemicals are added | Spencer Rizer | Logan Moore | 2026-06-11
Once the mix is done, the tank will circulate through the MS & MD valves for 30 minutes, or until the circulate is stopped | Spencer Rizer | Logan Moore | 2026-06-11
A tank is circulated through the MS and MD valves, with the mix pump opening on a 3 second delay | Spencer Rizer | Logan Moore | 2026-06-11
FULL MIX CHECKS
Uninterrupted Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-11
Uninterrupted Sequence 3 | Spencer Rizer | Logan Moore | 2026-06-11
Alarm Shutdown Sequence 1 | Spencer Rizer | Logan Moore | 2026-06-11
Alarm Shutdown Sequence 2 | Spencer Rizer | Logan Moore | 2026-06-11
ALL CHEMICALS
MCA Calculation Correct | Spencer Rizer |  | 2026-06-12
HE14 Calculation Correct | Spencer Rizer |  | 2026-06-12
HE45 Calculation Correct | Spencer Rizer |  | 2026-06-12
WAX Calculation Correct | Spencer Rizer |  | 2026-06-12

## SCADA Sign Off
SCADA SIGN-OFF
| UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | COMMENTS
Charge Entry Page
Correct charge number is used on 1st PTS charge and then sequential
Can enter and save all tally information manual or by scanner
BF/CF calculate correctly
Can print placards from page
Clear All Items and Delete Selected buttons function as intended
Shift selection is selected by operator and default value is prior charge treated
Code builder displays all selections needed to create charge
Treat Type selected pulls Cylinder, tank, UC, Solution Target from Treatment Type Settings
Can edit tally and save edit and footage calculates correctly after edit
Mix Pages
Correct current and target load on slide out menu
Spikes are applied to moldicides when mixes are loaded
Cannot load a charge to mix that has already been mixed
Required amounts calculate correctly and all work tanks configured for correct chemicals
Mix process page displays accurate graphic, tank info and scale weights
Active Mix system alarm button displays alarms
Min Volume to Treat calculation is accurate
Verify min required values prevent mix and exceeding max values doesn't allow mix
Accurately mix and display all mix info for each mix system - as mixed value, actual, timer
Cylinder Pages
All Status info displays correctly when charge is loaded
Plant cannot load and start a charge number already treated
Change Charge button - only charges entered and saved and not treated display on slider menu
Interlock safeties work and prevent starting a charge if that condition exists
Starting work tank volume locks in correctly when charge is started
Eco treatments have place to enter actual eco color PPM along with eco solution PPM
One click on steps to display detail for that step
Can edit cycle settings from edit button and changes are applied
Live injection and retention values are accurate
Trend chart is functional for each cylinder
Active alarm button displays all alarms associated with given cylinder
Door safeties accurately display on graphic the status of the cylinder doors
Liquid sensors or cylinder level radar accurately display conditions on graphic
Refresh CF button works if tally is edited while treating
Tank scaling and color schematic is accurate
PSI displays correctly based on pressure transmitter on cylinders for both pressure and vacuum
All valves and pumps can be operated in manual mode
Cylinder process graphic is accurate for each cylinder
Quality Control/Post Treatment Page
Solution results update correctly when entered on cylinder control page while treating
Solution results can be entered and saved if entered here after charge finishes
All Chemical Usage Info calculates correctly - Verified using spreadsheet from WPD
Wood QC can be entered and saves and calculated correctly with correct QC factors
Calculations are automatic when charge finishes and don't require hitting save button
ECO calculates cobiocide (imidicloprid)
Charge Reports
Gauge, Lbs and finish solutions are all calculating accurately for all chemicals
Wood assay results calculate correctly
Charge number list displays in descending order
Step reasons are accurate for condition that cause the step to advance
Run time correctly displays time the step actually ran (excludes pauses)
Strip factors, spike values and wood QC factors are accurate
Units displayed are correct for each chemical
Material Treated Info is complete and accurate
No missing or incorrect step detail info (time, pressure, injection, reten, volume, time
Can print charge reports
Mix information displays all relevant mix information
All header info is accurate
Admin
Chemicals Table displays all chemicals and has accurate % active, density and units
Mix Config - All k-factors are listed and used for mixes both auto or manual
Operator table - Plant can edit operator names
QC and strip factors are displayed and used for calculations from this table
Tank Default - All tank info is accurate and all tanks listed
Work Tank Tank Default - Correctly updates after mix, when results is entered while treated and when the charge finishes. All relevant chems displayed and tank settings are dialed in.
Treat table - Correct voids displayed and CF min max set correctly.
Treatment Entry - Can create cycle for each cylinder/tank and edit as needed
Tank Alarm setpoints are set correctly based on tank sizes
Corporate DB - Plant can import product codes, treat codes and yards from MSR
Tank Level setpoints - Scaled min/max and offsets are correct
Tank circulation - Tanks can be scheduled to circulate if applicable
TAT Display
TAT Monitor scales correctly on monitor on pad (if applicable)
TAT display info is accurate
Computers
Correct date & time is set on both computers
Shortcuts created on desktop for PTS and TAT Monitor
Verify LogMeIn is setup and functional
Run PTS from both computers successfully
Charges transfer to MSR for production reporting accurately

## New Program IO List
Punchlist | Integrator | Client | Scada | Date | Instr Type | Number | IO Tag | Description | MinEU | MaxEU | Units | LLSP | LSP | HSP | HHSP | Alarm State | Rack | Slot | Channel | Notes | Timer | Dbounce | Baud Rate | Parity | Stop Bits | Node | MIN Scaled | Max Scale | OFFset
|  | LM/RV |  |  | DI |  | ESRMonitor_In | [9 empty] | MAIN 0 | 1 | 0
|  | LM/RV |  |  | DI |  | FldEmergency1_In | [9 empty] | MAIN 0 | 1 | 1
|  | LM/RV |  |  | DI |  | FldEmergency2_In | [9 empty] | MAIN 0 | 1 | 2
|  | LM/RV |  |  | DI |  | FldEmergency3_In | [9 empty] | MAIN 0 | 1 | 3
|  | LM/RV |  |  | DI |  | FldEmergency4_In | [9 empty] | MAIN 0 | 1 | 4
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 1 | 5
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 1 | 6
|  | LM/RV |  |  | DI |  | PowerFail_In | [9 empty] | MAIN 0 | 1 | 7
|  | LM/RV |  |  | DO |  | ESDReset_Out | [9 empty] | MAIN 0 | 1 | 16
|  | LM/RV |  |  | DO |  | FldHorn1_Out | [9 empty] | MAIN 0 | 1 | 17
[5 empty] | DO |  | DNE | FldHorn2_Out | [8 empty] | MAIN 0 | 1 | 18
[5 empty] | DO |  | DNE | RedLight_Out | [8 empty] | MAIN 0 | 1 | 19
[5 empty] | DO |  | DNE | GreenLight_Out | [8 empty] | MAIN 0 | 1 | 20
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 1 | 21
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 1 | 22
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 1 | 23
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 0
|  | LM/RV |  |  | DI |  | Treat1_OverPSIsw_In | [9 empty] | MAIN 0 | 2 | 1
|  | LM/RV |  |  | DI |  | Treat1_StripEmptysw_In | [9 empty] | MAIN 0 | 2 | 2
|  | LM/RV |  |  | DI |  | WT2_Overflowsw_In | [9 empty] | MAIN 0 | 2 | 3 | Unable to check device. Checked alarm and interlocks from panel.
|  | LM/RV |  |  | DI |  | Treat1_Liquidsw_In | [9 empty] | MAIN 0 | 2 | 4
|  | LM/RV |  |  | DI |  | WT1_Overflowsw_In | [9 empty] | MAIN 0 | 2 | 5 | Unable to check device. Checked alarm and interlocks from panel.
|  | LM/RV |  |  | DI |  | Treat1_Fullsw_In | [9 empty] | MAIN 0 | 2 | 6
|  | LM/RV |  |  | DI |  | Treat1_Door1LeverClosed_In | [9 empty] | MAIN 0 | 2 | 7
|  | LM/RV |  |  | DI |  | LowAirPress_In | [9 empty] | MAIN 0 | 2 | 8
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 9
|  | LM/RV |  |  | DI |  | Water1_Overflowsw_In | [9 empty] | MAIN 0 | 2 | 10 | Unable to check device. Checked alarm and interlocks from panel.
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 11
|  | LM/RV |  |  | DI |  | WT3_Overflowsw_In | [9 empty] | MAIN 0 | 2 | 12 | Unable to check device. Checked alarm and interlocks from panel.
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 13
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 14
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 2 | 15
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 0
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 1
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 2
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 3
|  | LM/RV |  |  | DI |  | Water2_Overflowsw_In | [9 empty] | MAIN 0 | 3 | 4 | Unable to check device. Checked alarm and interlocks from panel.
|  | LM/RV |  |  | DI |  | WT6_Overflowsw_In | [9 empty] | MAIN 0 | 3 | 5 | Unable to check device. Checked alarm and interlocks from panel.
|  | LM/RV |  |  | DI |  | Treat1_AlmostFullsw_In | [9 empty] | MAIN 0 | 3 | 6
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 7
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 8
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 9
[5 empty] | DI |  | DNE | Pit 1 Level Control | [8 empty] | MAIN 0 | 3 | 10
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 11
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 12
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 13
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 14
[5 empty] | DI |  | Spare | [9 empty] | MAIN 0 | 3 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 0
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 3
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 5
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 7
|  | LM/RV |  |  | DO |  | Treat1_V1vlv_Out | [9 empty] | MAIN 0 | 4 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 4 | 12
|  | LM/RV |  |  | DO |  | CWM1_2_vlv_Out | Mix1_M7vlv_Out | [8 empty] | MAIN 0 | 4 | 13
|  | LM/RV |  |  | DO |  | Treat1_Transfer1pmp_Out | [9 empty] | MAIN 0 | 4 | 14
|  | LM/RV |  |  | DO |  | Treat1_Transfer2pmp_Out | [9 empty] | MAIN 0 | 4 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 0
|  | LM/RV |  |  | DO |  | MOLDACpmp_Out | [9 empty] | MAIN 0 | 5 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 3
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 5
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 5 | 14
|  | LM/RV |  |  | DO |  | MCApmp1_Out | [9 empty] | MAIN 0 | 5 | 15
|  | LM/RV |  |  | DO |  | MOLDAC1_2_vlv_Out | Mix1_M4vlv_Out | [8 empty] | MAIN 0 | 6 | 0
|  | LM/RV |  |  | DO |  | Treat1_Doorpitsumppmp_Out | [9 empty] | MAIN 0 | 6 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 3
|  | LM/RV |  |  | DO |  | Treat1_Strippmp1_Out | [9 empty] | MAIN 0 | 6 | 4
|  | LM/RV |  |  | DO |  | Treat1_Vacpmp1_Out | [9 empty] | MAIN 0 | 6 | 5
|  | LM/RV |  |  | DO |  | Treat1_Vacpmp2_Out | [9 empty] | MAIN 0 | 6 | 6
|  | LM/RV |  |  | DO |  | Treat1_Doorpump_Out | [9 empty] | MAIN 0 | 6 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 6 | 14
|  | LM/RV |  |  | DO |  | Treat2_TnkV6vlv_Out | [9 empty] | MAIN 0 | 6 | 15
|  | LM/RV |  |  | DO |  | Treat2_R6vlv_Out | [9 empty] | MAIN 0 | 7 | 0
|  | LM/RV |  |  | DO |  | MCApmp2_Out | [9 empty] | MAIN 0 | 7 | 1
|  | LM/RV |  |  | DO |  | Treat2_C2vlv_Out | [9 empty] | MAIN 0 | 7 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 3
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 5
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 7 | 14
|  | LM/RV |  |  | DO |  | Mixpmp1_Out | [9 empty] | MAIN 0 | 7 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 0
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 3
|  | LM/RV |  |  | DO |  | MCA_Recirc_Out | [9 empty] | MAIN 0 | 8 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 5
|  | LM/RV |  |  | DO |  | Treat2_C3vlv_Out | [9 empty] | MAIN 0 | 8 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 8
[5 empty] | DO |  | DNE | Mix1_M8vlv_Out | [8 empty] | MAIN 0 | 8 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 14
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 8 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 0
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 3
[5 empty] | DO |  | DNE | Mix1_M5-3vlv_Out | [8 empty] | MAIN 0 | 9 | 4
|  | LM/RV |  |  | DO |  | CWM2_vlv_Out | Mix1_M7-3vlv_Out | [8 empty] | MAIN 0 | 9 | 5
[5 empty] | DO |  | DNE | Mix1_M5-4vlv_Out | [8 empty] | MAIN 0 | 9 | 6
|  | LM/RV |  |  | DO |  | CWM3_vlv_Out | Mix1_M7-4vlv_Out | [8 empty] | MAIN 0 | 9 | 7
|  | LM/RV |  |  | DO |  | CWMpmp_Out | [9 empty] | MAIN 0 | 9 | 8
[5 empty] | DO |  | PROBABLY NANI (DNE) | [9 empty] | MAIN 0 | 9 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 10
|  | LM/RV |  |  | DO |  | Wellpmp_Out | [9 empty] | MAIN 0 | 9 | 11
|  | LM/RV |  |  | DO |  | MOLDAC2_2_vlv_Out | Mix1_M4-3Avlv_Out | [8 empty] | MAIN 0 | 9 | 12
|  | LM/RV |  |  | DO |  | MOLDAC3_2_vlv_Out | Mix1_M4-4Avlv_Out | [8 empty] | MAIN 0 | 9 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 14
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 9 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 0
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 3
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 5
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 14
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 10 | 15
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 0
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 1
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 2
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 3
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 4
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 5
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 6
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 7
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 8
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 9
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 10
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 11
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 12
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 13
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 14
[5 empty] | DO |  | Spare | [9 empty] | MAIN 0 | 11 | 15
|  | LM/RV |  |  | AI |  | Treat1 PSI | [9 empty] | MAIN 1 | 0 | 0
|  | LM/RV |  |  | AI |  | WT6 Level | [9 empty] | MAIN 1 | 0 | 1 | As good as it can be. Need to verify at lower levels
|  | LM/RV |  |  | AI |  | WT1 Level | [9 empty] | MAIN 1 | 0 | 2
[5 empty] | AI |  | Spare | [9 empty] | MAIN 1 | 0 | 3
|  | LM/RV |  |  | AI |  | Water 1 Level | [9 empty] | MAIN 1 | 0 | 4 | As good as it can be. Need to verify at higher levels
|  | LM/RV |  |  | AI |  | WT2 Level | [9 empty] | MAIN 1 | 0 | 5
|  | LM/RV |  |  | AI |  | Water 2 Level | [9 empty] | MAIN 1 | 0 | 6 | As good as it can be. Need to verify at higher levels
|  | LM/RV |  |  | AI |  | MCA Level | [9 empty] | MAIN 1 | 0 | 7 | As good as it can be. Need to verify at lower levels
|  | LM/RV |  |  | AI |  | WT3 Level | [9 empty] | MAIN 1 | 1 | 0
[5 empty] | AI |  | Spare | [9 empty] | MAIN 1 | 1 | 1
[5 empty] | AI |  | Spare | [9 empty] | MAIN 1 | 1 | 2
[5 empty] | AI |  | Spare | [9 empty] | MAIN 1 | 1 | 3
|  | LM/RV |  |  | AO |  | Treat1 Control Valve | [9 empty] | MAIN 1 | 1 | 4
[5 empty] | AO |  | Spare | [9 empty] | MAIN 1 | 1 | 5
|  | LM/RV |  |  | Counter |  | MCA 1 Flow | [9 empty] | MAIN 1 | 2 | 0
|  | LM/RV |  |  | Counter |  | MCA 2 Flow | [9 empty] | MAIN 1 | 2 | 2
|  | LM/RV |  |  | Counter |  | MoldAC Flow | [9 empty] | MAIN 1 | 2 | 4
[5 empty] | Counter |  | Spare | [9 empty] | MAIN 1 | 2 | 6
|  | LM/RV |  |  | DI |  | PowerFail2_In | [9 empty] | Remote 0 | 1 | 0
|  | LM/RV |  |  | DI |  | Treat2_OverPSIsw_In | [9 empty] | Remote 0 | 1 | 1 | Unsafe to access. Tested from panel.
|  | LM/RV |  |  | DI |  | Treat2_AlmostFullsw_In | [9 empty] | Remote 0 | 1 | 2
|  | LM/RV |  |  | DI |  | Treat2_Fullsw_In | [9 empty] | Remote 0 | 1 | 3
[5 empty] | DI |  | DNE | Hydraulic Pump Run Status (NOT IN USE IN OLD PLC) | [8 empty] | Remote 0 | 1 | 4
|  | LM/RV |  |  | DI |  | Treat2_Door1LeverClosed_In | [9 empty] | Remote 0 | 1 | 5
|  | LM/RV |  |  | DI |  | Treat2_StripEmptysw_In | [9 empty] | Remote 0 | 1 | 6
|  | LM/RV |  |  | DI |  | Treat2_Liquidsw_In | [9 empty] | Remote 0 | 1 | 7
|  | LM/RV |  |  | DI |  | Pit 3 Level Control | [9 empty] | Remote 0 | 1 | 8
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 1 | 9
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 1 | 10
|  | LM/RV |  |  | DI |  | Pit 4 Level Control | [9 empty] | Remote 0 | 1 | 11
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 1 | 12
|  | LM/RV |  |  | DI |  | WT4_Overflowsw_In | [9 empty] | Remote 0 | 1 | 13 | Unsafe to access. Tested from panel.
|  | LM/RV |  |  | DI |  | WT5_Overflowsw_In | [9 empty] | Remote 0 | 1 | 14 | Unsafe to access. Tested from panel.
|  | LM/RV |  |  | DI |  | Pit 2 Level Control | [9 empty] | Remote 0 | 1 | 15
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 0
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 1
[5 empty] | DI |  | DNE | Unloading Pump Flow Sw | [8 empty] | Remote 0 | 2 | 2
[5 empty] | DI |  | DNE | Hydraulic Pump Stop Sw 2 | [8 empty] | Remote 0 | 2 | 3
[5 empty] | DI |  | DNE | Unloading Pump Stop Sw | [8 empty] | Remote 0 | 2 | 4
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 5
|  | LM/RV |  |  | DI |  | Wax_Overflowsw_In | [9 empty] | Remote 0 | 2 | 6 | Unsafe to access. Tested from panel.
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 7
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 8
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 9
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 10
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 11
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 12
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 13
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 14
[5 empty] | DI |  | Spare | [9 empty] | Remote 0 | 2 | 15
|  | LM/RV |  |  | DO |  | Mix2pmp_Out | Mixpmp3_Out | [8 empty] | Remote 0 | 3 | 0
|  | LM/RV |  |  | DO |  | Treat2_Presspmp1_Out | [9 empty] | Remote 0 | 3 | 1
|  | LM/RV |  |  | DO |  | Treat2_Presspmp2_Out | [9 empty] | Remote 0 | 3 | 2
|  | LM/RV |  |  | DO |  | Treat2_Transpmp1_Out | [9 empty] | Remote 0 | 3 | 3
[5 empty] | DO |  | DNE | Mix1_M9-4vlv_Out | [8 empty] | Remote 0 | 3 | 4
|  | LM/RV |  |  | DO |  | Treat2_Strippmp_Out | [9 empty] | Remote 0 | 3 | 5
|  | LM/RV |  |  | DO |  | Treat2_Vacpmp1_Out | [9 empty] | Remote 0 | 3 | 6
|  | LM/RV |  |  | DO |  | Treat2_SealWaterpmp_Out | [9 empty] | Remote 0 | 3 | 7
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 3 | 8
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 3 | 9
[5 empty] | DO |  | UnloadingPadSumppmp_Out (DNE) | [9 empty] | Remote 0 | 3 | 10
|  | LM/RV |  |  | DO |  | Treat2_DoorpitSumppmp_Out | [9 empty] | Remote 0 | 3 | 11
|  | LM/RV |  |  | DO |  | Treat2_Doorpmp_Out | [9 empty] | Remote 0 | 3 | 12
|  | LM/RV |  |  | DO |  | Treat2_T1vlv_Out | [9 empty] | Remote 0 | 3 | 13
|  | LM/RV |  |  | DO |  | Treat2_T2vlv_Out | [9 empty] | Remote 0 | 3 | 14
|  | LM/RV |  |  | DO |  | Treat2_T3vlv_Out | [9 empty] | Remote 0 | 3 | 15
|  | LM/RV |  |  | DO |  | Treat2_T4vlv_Out | [9 empty] | Remote 0 | 4 | 0
|  | LM/RV |  |  | DO |  | Treat2_P1vlv_Out | [9 empty] | Remote 0 | 4 | 1
|  | LM/RV |  |  | DO |  | Treat2_P2vlv_Out | [9 empty] | Remote 0 | 4 | 2
|  | LM/RV |  |  | DO |  | Treat2_S1vlv_Out | [9 empty] | Remote 0 | 4 | 3
|  | LM/RV |  |  | DO |  | Treat2_S2vlv_Out | [9 empty] | Remote 0 | 4 | 4
|  | LM/RV |  |  | DO |  | Mix1_M12vlv_Out | Mix1_M1-3vlv_Out | [8 empty] | Remote 0 | 4 | 5
|  | LM/RV |  |  | DO |  | MOLDAC3_2_vlv_Out | Mix1_M4-4Bvlv_Out | [8 empty] | Remote 0 | 4 | 6
|  | LM/RV |  |  | DO |  | Mix1_M13vlv_Out | Mix1_M1-4vlv_Out | [8 empty] | Remote 0 | 4 | 7
|  | LM/RV |  |  | DO |  | MD4vlv_Out | [9 empty] | Remote 0 | 4 | 8
|  | LM/RV |  |  | DO |  | MD5vlv_Out | [9 empty] | Remote 0 | 4 | 9
|  | LM/RV |  |  | DO |  | MS4vlv_Out | [9 empty] | Remote 0 | 4 | 10
|  | LM/RV |  |  | DO |  | MS5vlv_Out | [9 empty] | Remote 0 | 4 | 11
|  | LM/RV |  |  | DO |  | Treat2_V1vlv_Out | [9 empty] | Remote 0 | 4 | 12
[5 empty] | DO |  | DNE | Treat2_V2vlv_Out | [8 empty] | Remote 0 | 4 | 13
[5 empty] | DO |  | DNE | Treat2_C1vlv_Out | [8 empty] | Remote 0 | 4 | 14
|  | LM/RV |  |  | DO |  | SV4_vlv_Out | [9 empty] | Remote 0 | 4 | 15
|  | LM/RV |  |  | DO |  | SV5_vlv_Out | [9 empty] | Remote 0 | 5 | 0
|  | LM/RV |  |  | DO |  | Treat2_Tnkv4vlv_Out | [9 empty] | Remote 0 | 5 | 1
|  | LM/RV |  |  | DO |  | Treat2_Tnkv5vlv_Out | [9 empty] | Remote 0 | 5 | 2
|  | LM/RV |  |  | DO |  | Treat2_SealWatervlv1_Out | [9 empty] | Remote 0 | 5 | 3
|  | LM/RV |  |  | DO |  | Treat2_SealWatervlv2_Out | [9 empty] | Remote 0 | 5 | 4
|  | LM/RV |  |  | DO |  | Waxpmp_Out | [9 empty] | Remote 0 | 5 | 5
|  | LM/RV |  |  | DO |  | Mix3pmp_Out | Mixpmp4_Out | [8 empty] | Remote 0 | 5 | 6
|  | LM/RV |  |  | DO |  | WAX2_vlv_Out | Mix1_M3-3vlv_Out | [8 empty] | Remote 0 | 5 | 7
|  | LM/RV |  |  | DO |  | MCA2_vlv_Out | Mix1_M2-3vlv_Out | [8 empty] | Remote 0 | 5 | 8
|  | LM/RV |  |  | DO |  | Treat2_R5vlv_Out | [9 empty] | Remote 0 | 5 | 9
|  | LM/RV |  |  | DO |  | Treat2_R4vlv_Out | [9 empty] | Remote 0 | 5 | 10
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 5 | 11
|  | LM/RV |  |  | DO |  | TankFarmSumppmp_Out | [9 empty] | Remote 0 | 5 | 12
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 5 | 13
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 5 | 14
|  | LM/RV |  |  | DO |  | Treat2_Transpmp2_Out | [9 empty] | Remote 0 | 5 | 15
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 6 | 0
|  | LM/RV |  |  | DO |  | MS6vlv_Out | [9 empty] | Remote 0 | 6 | 1
|  | LM/RV |  |  | DO |  | SV10_vlv_Out | [9 empty] | Remote 0 | 6 | 2
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 6 | 3
|  | LM/RV |  |  | DO |  | MCA3vlv_Out | Mix1_M2-4vlv_Out | [8 empty] | Remote 0 | 6 | 4
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 6 | 5
|  | LM/RV |  |  | DO |  | Treat2_T6vlv_Out | [9 empty] | Remote 0 | 6 | 6
|  | LM/RV |  |  | DO |  | Treat2_T5vlv_Out | [9 empty] | Remote 0 | 6 | 7
|  | LM/RV |  |  | DO |  | MOLDAC2_2_vlv_Out | Mix1_M4-3Bvlv_Out | [8 empty] | Remote 0 | 6 | 8
|  | LM/RV |  |  | DO |  | MD6vlv_Out | [9 empty] | Remote 0 | 6 | 9
|  | LM/RV |  |  | DO |  | Treat2_S3vlv_Out | [9 empty] | Remote 0 | 6 | 10
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 6 | 11
[5 empty] | DO |  | DNE | Mix1_M8-4vlv_Out | [8 empty] | Remote 0 | 6 | 12
|  | LM/RV |  |  | DO |  | Treat2_T7vlv_Out | [9 empty] | Remote 0 | 6 | 13
|  | LM/RV |  |  | DO |  | SV9_vlv_Out (SV8 When output off) | [9 empty] | Remote 0 | 6 | 14
[5 empty] | DO |  | Treat2_F1vlv_Out (DNE) | [9 empty] | Remote 0 | 6 | 15
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 0
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 1
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 2
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 3
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 4
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 5
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 6
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 7
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 8
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 9
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 10
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 11
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 12
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 13
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 14
[5 empty] | DO |  | Spare | [9 empty] | Remote 0 | 7 | 15
|  | LM/RV |  |  | AI |  | Treat2 PSI | [9 empty] | Remote 1 | 1 | 0
|  | LM/RV |  |  | AI |  | WT4 Level | [9 empty] | Remote 1 | 1 | 1
|  | LM/RV |  |  | AI |  | WT5 Level | [9 empty] | Remote 1 | 1 | 2 | NEED TO VERIFY AT HIGHER LEVELS
[5 empty] | AI |  | OLD Process Tank (DNE) | [9 empty] | Remote 1 | 1 | 3
|  | LM/RV |  |  | AI |  | WAX Level | [9 empty] | Remote 1 | 1 | 4 | NEED TO VERIFY AT LOWER LEVELS
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 1 | 5
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 1 | 6
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 1 | 7
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 0
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 1
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 2
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 3
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 4
[5 empty] | AI |  | Spare | [9 empty] | Remote 1 | 2 | 5
|  | LM/RV |  |  | AO |  | Treat2 Control Valve | [9 empty] | Remote 1 | 2 | 6 | Needs calibrated in field
[5 empty] | AO |  | Spare | [9 empty] | Remote 1 | 2 | 7
[5 empty] | Counter |  | Nani Flow (DNE) | [9 empty] | Remote 1 | 3 | 0
[5 empty] | Counter |  | Unknown (DNE) | [9 empty] | Remote 1 | 3 | 2
|  | LM/RV |  |  | Counter |  | CWM Flow | [9 empty] | Remote 1 | 3 | 4
[5 empty] | Counter |  | Unknown (DNE) | [9 empty] | Remote 1 | 3 | 6
|  | LM/RV |  |  | Counter |  | WAX Flow | [9 empty] | Remote 1 | 4 | 0
[5 empty] | Counter |  | Spare | [9 empty] | Remote 1 | 4 | 2
[5 empty] | Counter |  | Spare | [9 empty] | Remote 1 | 4 | 4
[5 empty] | Counter |  | Spare | [9 empty] | Remote 1 | 4 | 6
|  | LM/RV |  |  | DO |  | Treat1_Presspmp1_Out | [9 empty] | ETH | - | -
|  | LM/RV |  |  | DO |  | Treat1_Presspmp2_Out | [9 empty] | ETH | - | -
|  | LM/RV |  |  | AO |  | Treat1_Presspmp1_Speed | [9 empty] | ETH | - | -
|  | LM/RV |  |  | AO |  | Treat1_Presspmp2_Speed | [9 empty] | ETH | - | -
|  | LM/RV |  |  | DO |  | Treat1_P2vlv_Out | [9 empty] | VALVE PANEL 1 | - | S1
|  | LM/RV |  |  | DO |  | Treat1_P1vlv_Out | [9 empty] | VALVE PANEL 1 | - | S2
|  | LM/RV |  |  | DO |  | Treat1_P4vlv_Out | [9 empty] | VALVE PANEL 1 | - | S3
|  | LM/RV |  |  | DO |  | Treat1_P3vlv_Out | [9 empty] | VALVE PANEL 1 | - | S4
|  | LM/RV |  |  | DO |  | Treat1_T3vlv_Out | [9 empty] | VALVE PANEL 1 | - | S5
|  | LM/RV |  |  | DO |  | Treat1_T2vlv_Out | [9 empty] | VALVE PANEL 1 | - | S6
|  | LM/RV |  |  | DO |  | Treat1_T1vlv_Out | [9 empty] | VALVE PANEL 1 | - | S7
|  | LM/RV |  |  | DO |  | Treat1_T4vlv_Out | [9 empty] | VALVE PANEL 1 | - | S8
|  | LM/RV |  |  | DO |  | Treat1_S1vlv_Out | [9 empty] | VALVE PANEL 1 | - | S9
|  | LM/RV |  |  | DO |  | Treat1_S2vlv_Out | [9 empty] | VALVE PANEL 1 | - | S10
|  | LM/RV |  |  | DO |  | Treat1_T5vlv_Out | [9 empty] | VALVE PANEL 1 | - | S11
|  | LM/RV |  |  | DO |  | MCA1_vlv_Out | Mix1_M2-2vlv_Out | [8 empty] | VALVE PANEL 1 | - | S12
|  | LM/RV |  |  | DO |  | CWM1_vlv_Out | Mix1_M7-2vlv_Out | [8 empty] | VALVE PANEL 1 | - | S13
[5 empty] | DO |  | DNE | Mix1_M5-2vlv_Out | [8 empty] | VALVE PANEL 1 | - | S14
|  | LM/RV |  |  | DO |  | MOLDAC1_vlv_Out | Mix1_M4-2vlv_Out | [8 empty] | VALVE PANEL 1 | - | S15
|  | LM/RV |  |  | DO |  | WAX1_vlv_Out | Mix1_M3-2vlv_Out | [8 empty] | VALVE PANEL 1 | - | S16
|  | LM/RV |  |  | DO |  | Treat1_R1vlv_Out | [9 empty] | VALVE PANEL 2 | - | S1
|  | LM/RV |  |  | DO |  | MD1vlv_Out | [9 empty] | VALVE PANEL 2 | - | S2
|  | LM/RV |  |  | DO |  | MS1vlv_Out | [9 empty] | VALVE PANEL 2 | - | S3
|  | LM/RV |  |  | DO |  | Treat1_TnkV1vlv_Out | [9 empty] | VALVE PANEL 2 | - | S4
|  | LM/RV |  |  | DO |  | Treat1_R2vlv_Out | [9 empty] | VALVE PANEL 2 | - | S5
|  | LM/RV |  |  | DO |  | MD2vlv_Out | [9 empty] | VALVE PANEL 2 | - | S6
|  | LM/RV |  |  | DO |  | MS2vlv_Out | [9 empty] | VALVE PANEL 2 | - | S7
|  | LM/RV |  |  | DO |  | Treat1_TnkV2vlv_Out | [9 empty] | VALVE PANEL 2 | - | S8
|  | LM/RV |  |  | DO |  | Treat1_R3vlv_Out | [9 empty] | VALVE PANEL 2 | - | S9
|  | LM/RV |  |  | DO |  | MD3vlv_Out | [9 empty] | VALVE PANEL 2 | - | S10
|  | LM/RV |  |  | DO |  | MS3vlv_Out | [9 empty] | VALVE PANEL 2 | - | S11
|  | LM/RV |  |  | DO |  | Treat1_TnkV3vlv_Out | [9 empty] | VALVE PANEL 2 | - | S12
|  | LM/RV |  |  | DO |  | Water1vlv_Out | [9 empty] | VALVE PANEL 2 | - | S13
|  | LM/RV |  |  | DO |  | Water2vlv_Out | [9 empty] | VALVE PANEL 2 | - | S14
|  | LM/RV |  |  | DO |  | Mix1_M11vlv_Out | [9 empty] | VALVE PANEL 2 | - | S15
[5 empty] | DO |  | Spare | [9 empty] | VALVE PANEL 2 | - | S16

## Old Program IO List
Wiring Configuration | Temp Wire Number | Signal | Old Tag | New Tag | Description | Raw Min | Raw Max | Scaled Min | Scaled Max | DI Signal States | Rack | Slot | Channel | Notes
|  | DI |  | ESRMonitor_In | ESR Monitor | [5 empty] | MAIN 0 | 1 | 0
|  | DI |  | FldEmergency1_In | ESD 1 | [5 empty] | MAIN 0 | 1 | 1
|  | DI |  | FldEmergency2_In | ESD 2 | [5 empty] | MAIN 0 | 1 | 2
|  | DI |  | FldEmergency3_In | ESD3 | [5 empty] | MAIN 0 | 1 | 3
|  | DI |  | FldEmergency4_In | ESD 4 | [5 empty] | MAIN 0 | 1 | 4
|  | DI |  | Spare | [6 empty] | MAIN 0 | 1 | 5
|  | DI |  | Spare | [6 empty] | MAIN 0 | 1 | 6
|  | DI |  | PowerFail_In | OUTPUT CHECK | [5 empty] | MAIN 0 | 1 | 7
|  | DO |  | ESDReset_Out | ESD Reset | [5 empty] | MAIN 0 | 1 | 16
|  | DO |  | FldHorn1_Out | Horn 1 | [5 empty] | MAIN 0 | 1 | 17
|  | DO |  | FldHorn2_Out | Horn2 | [5 empty] | MAIN 0 | 1 | 18 | Does not work
|  | DO |  | RedLight_Out | red Light | [5 empty] | MAIN 0 | 1 | 19
|  | DO |  | GreenLight_Out | Green light | [5 empty] | MAIN 0 | 1 | 20
|  | DO |  | Spare | [6 empty] | MAIN 0 | 1 | 21
|  | DO |  | Spare | [6 empty] | MAIN 0 | 1 | 22
|  | DO |  | Spare | [6 empty] | MAIN 0 | 1 | 23
|  | DI |  | Spare | [6 empty] | MAIN 0 | 2 | 0
|  | DI |  | Treat1_OverPSIsw_In | Treat1 Over PSI | [5 empty] | MAIN 0 | 2 | 1
|  | DI |  | Treat1_StripEmptysw_In | Treat 2 Strip Empty | [5 empty] | MAIN 0 | 2 | 2
|  | DI |  | WT2_Overflowsw_In | Tank2 Overflow | [5 empty] | MAIN 0 | 2 | 3
|  | DI |  | Treat1_Liquidsw_In | Treat 1 Liquid Switch | [5 empty] | MAIN 0 | 2 | 4
|  | DI |  | WT1_Overflowsw_In | Tank 1 Overflow | [5 empty] | MAIN 0 | 2 | 5
|  | DI |  | Treat1_Fullsw_In | Treat1 Full | [5 empty] | MAIN 0 | 2 | 6
|  | DI |  | Treat1_Door1LeverClosed_In | Treat 1 Door lever | [5 empty] | MAIN 0 | 2 | 7
|  | DI |  | LowAirPress_In | Low Air | [5 empty] | MAIN 0 | 2 | 8
|  | DI |  | Spare | Tank 12 full | [5 empty] | MAIN 0 | 2 | 9
|  | DI |  | Water1_Overflowsw_In | Tank 12 Over flow | [5 empty] | MAIN 0 | 2 | 10
|  | DI |  | Spare | [6 empty] | MAIN 0 | 2 | 11
|  | DI |  | WT3_Overflowsw_In | Tank 3 Overflow | [5 empty] | MAIN 0 | 2 | 12
|  | DI |  | Spare | Tank 21 Overflow | [5 empty] | MAIN 0 | 2 | 13
|  | DI |  | Spare | [6 empty] | MAIN 0 | 2 | 14
|  | DI |  | Spare | Tank 21 Empty | [5 empty] | MAIN 0 | 2 | 15
|  | DI |  | Spare | Well ON | [5 empty] | MAIN 0 | 3 | 0
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 1
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 2
|  | DI |  | Spare | Well OFF | [5 empty] | MAIN 0 | 3 | 3
|  | DI |  | Water2_Overflowsw_In | Tank 14 Overflow | [5 empty] | MAIN 0 | 3 | 4
|  | DI |  | WT6_Overflowsw_In | Tank 6 Overflow | [5 empty] | MAIN 0 | 3 | 5
|  | DI |  | Treat1_AlmostFullsw_In | Treat 1 Alost Full | [5 empty] | MAIN 0 | 3 | 6
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 7
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 8
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 9
|  | DI |  | Pit 1 Level Control | PIT LEVEL Control | [5 empty] | MAIN 0 | 3 | 10
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 11
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 12
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 13
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 14
|  | DI |  | Spare | [6 empty] | MAIN 0 | 3 | 15
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 1
|  | DO |  | Spare | M4 | [5 empty] | MAIN 0 | 4 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 3
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 4
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 5
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 6
|  | DO |  | Spare | V2_1 | [5 empty] | MAIN 0 | 4 | 7
|  | DO |  | Treat1_V1vlv_Out | V1_1 | [5 empty] | MAIN 0 | 4 | 8
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 10
|  | DO |  | Spare | S3_1 | [5 empty] | MAIN 0 | 4 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 4 | 12
|  | DO |  | Mix1_M7vlv_Out | M7A_1 | [5 empty] | MAIN 0 | 4 | 13
|  | DO |  | Treat1_Transfer1pmp_Out | Transfer1_1 | [5 empty] | MAIN 0 | 4 | 14
|  | DO |  | Treat1_Transfer2pmp_Out | Transfer2_1 | [5 empty] | MAIN 0 | 4 | 15
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 0
|  | DO |  | MOLDACpmp_Out | MOldAc_1 | [5 empty] | MAIN 0 | 5 | 1
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 3
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 4
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 5
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 6
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 7
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 8
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 10
|  | DO |  | Spare | M2_1 | [5 empty] | MAIN 0 | 5 | 11
|  | DO |  | Spare | m11_1 | [5 empty] | MAIN 0 | 5 | 12
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 5 | 14
|  | DO |  | MCApmp1_Out | mca1-1 | [5 empty] | MAIN 0 | 5 | 15
|  | DO |  | Mix1_M4vlv_Out | M4A_1 | [5 empty] | MAIN 0 | 6 | 0
|  | DO |  | Treat1_Doorpitsumppmp_Out | TREAT1DOOR pit | [5 empty] | MAIN 0 | 6 | 1
|  | DO |  | Spare | Presspump3 | [5 empty] | MAIN 0 | 6 | 2
|  | DO |  | Spare | presspump4 | [5 empty] | MAIN 0 | 6 | 3
|  | DO |  | Treat1_Strippmp1_Out | strip pump1-1 | [5 empty] | MAIN 0 | 6 | 4
|  | DO |  | Treat1_Vacpmp1_Out | vac pump1-1 | [5 empty] | MAIN 0 | 6 | 5
|  | DO |  | Treat1_Vacpmp2_Out | vac pump2-1 | [5 empty] | MAIN 0 | 6 | 6
|  | DO |  | Treat1_Doorpump_Out | Hydraulic Pump1-1 | [5 empty] | MAIN 0 | 6 | 7
|  | DO |  | Spare | [6 empty] | MAIN 0 | 6 | 8
|  | DO |  | Spare | [6 empty] | MAIN 0 | 6 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 6 | 10
|  | DO |  | Spare | Tankv13-1 | [5 empty] | MAIN 0 | 6 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 6 | 12
|  | DO |  | Spare | Eff pump-1 | [5 empty] | MAIN 0 | 6 | 13
|  | DO |  | Spare | Well pump secondary | [5 empty] | MAIN 0 | 6 | 14
|  | DO |  | Treat2_TnkV6vlv_Out | TNKv6-2 | [5 empty] | MAIN 0 | 6 | 15
|  | DO |  | Treat2_R6vlv_Out | R6-2 | [5 empty] | MAIN 0 | 7 | 0
|  | DO |  | MCApmp2_Out | mca2-1 | [5 empty] | MAIN 0 | 7 | 1
|  | DO |  | Treat2_C2vlv_Out | c2-2 | [5 empty] | MAIN 0 | 7 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 7 | 3
|  | DO |  | Spare | SV6-1 | [5 empty] | MAIN 0 | 7 | 4
|  | DO |  | Spare | [6 empty] | MAIN 0 | 7 | 5
|  | DO |  | Spare | w1-2-1 | [5 empty] | MAIN 0 | 7 | 6
|  | DO |  | Spare | [6 empty] | MAIN 0 | 7 | 7
|  | DO |  | Spare | C1-1 | [5 empty] | MAIN 0 | 7 | 8
|  | DO |  | Spare | SV1_1 | [5 empty] | MAIN 0 | 7 | 9
|  | DO |  | Spare | SV2_1 | [5 empty] | MAIN 0 | 7 | 10
|  | DO |  | Spare | SV3_1 | [5 empty] | MAIN 0 | 7 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 7 | 12
|  | DO |  | Spare | Not label | [5 empty] | MAIN 0 | 7 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 7 | 14
|  | DO |  | Mixpmp1_Out | MIx1-1 | [5 empty] | MAIN 0 | 7 | 15
MAIN 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 1
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 3
|  | DO |  | MCA_Recirc_Out | Not label | [5 empty] | MAIN 0 | 8 | 4
|  | DO |  | Spare | Mix2_1 | [5 empty] | MAIN 0 | 8 | 5
|  | DO |  | Treat2_C3vlv_Out | C3_2 | [5 empty] | MAIN 0 | 8 | 6
|  | DO |  | Spare | T6-1 | [5 empty] | MAIN 0 | 8 | 7
|  | DO |  | Spare | T7-1 | [5 empty] | MAIN 0 | 8 | 8
|  | DO |  | Mix1_M8vlv_Out | M8-1 | [5 empty] | MAIN 0 | 8 | 9
|  | DO |  | Spare | Wax_1 | [5 empty] | MAIN 0 | 8 | 10
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 12
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 14
|  | DO |  | Spare | [6 empty] | MAIN 0 | 8 | 15
MAIN 0
|  | DO |  | Spare | M5-1 | [5 empty] | MAIN 0 | 9 | 0
|  | DO |  | Spare | M7-1 | [5 empty] | MAIN 0 | 9 | 1
|  | DO |  | Spare | [6 empty] | MAIN 0 | 9 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 9 | 3
|  | DO |  | Mix1_M5-3vlv_Out | m35-1 | [5 empty] | MAIN 0 | 9 | 4
|  | DO |  | Mix1_M7-3vlv_Out | m37B-1 | [5 empty] | MAIN 0 | 9 | 5
|  | DO |  | Mix1_M5-4vlv_Out | M25-1 | [5 empty] | MAIN 0 | 9 | 6
|  | DO |  | Mix1_M7-4vlv_Out | m27B-1 | [5 empty] | MAIN 0 | 9 | 7
|  | DO |  | CWMpmp_Out | He45-1 | [5 empty] | MAIN 0 | 9 | 8
|  | DO |  | UNKNOWN (PROBABLY NANI) | nani_1 | [5 empty] | MAIN 0 | 9 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 9 | 10
|  | DO |  | Wellpmp_Out | well pump | [5 empty] | MAIN 0 | 9 | 11
|  | DO |  | Mix1_M4-3Avlv_Out | m34A_1 | [5 empty] | MAIN 0 | 9 | 12
|  | DO |  | Mix1_M4-4Avlv_Out | M24_1 | [5 empty] | MAIN 0 | 9 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 9 | 14
|  | DO |  | Spare | [6 empty] | MAIN 0 | 9 | 15
MAIN 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 1
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 3
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 4
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 5
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 6
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 7
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 8
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 10
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 12
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 14
|  | DO |  | Spare | [6 empty] | MAIN 0 | 10 | 15
MAIN 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 0
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 1
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 2
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 3
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 4
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 5
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 6
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 7
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 8
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 9
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 10
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 11
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 12
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 13
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 14
|  | DO |  | Spare | [6 empty] | MAIN 0 | 11 | 15
|  | AI |  | Treat1 PSI | Worktank 3 |  | Ani1 |  |  |  | MAIN 1 | 0 | 0
|  | AI |  | WT6 Level | Worktank 2 |  | Ani2 |  |  |  | MAIN 1 | 0 | 1
|  | AI |  | WT1 Level | water Tank 2 |  | Ani3 |  |  |  | MAIN 1 | 0 | 2
|  | AI |  | Spare | MCA Tank |  | Ani4 |  |  |  | MAIN 1 | 0 | 3
|  | AI |  | Water 1 Level | Water Tank 1 |  | Ani5 |  |  |  | MAIN 1 | 0 | 4
|  | AI |  | WT2 Level |  |  | Ani6 |  |  |  | MAIN 1 | 0 | 5
|  | AI |  | Water 2 Level |  |  | Ani7 |  |  |  | MAIN 1 | 0 | 6
|  | AI |  | MCA Level | NANI Scale |  | Ani8 |  |  |  | MAIN 1 | 0 | 7
|  | AI |  | WT3 Level | Cylinder 1 PSI |  | Ani9 |  |  |  | MAIN 1 | 1 | 0
|  | AI |  | Spare | Work tank 6 |  | Ani10 |  |  |  | MAIN 1 | 1 | 1
|  | AI |  | Spare | Work Tank 1 |  | Ani11 |  |  |  | MAIN 1 | 1 | 2
|  | AI |  | Spare |  |  | Ani12 |  |  |  | MAIN 1 | 1 | 3
|  | AO |  | Treat1 Control Valve | Cyl1 Control Valve | [5 empty] | MAIN 1 | 1 | 4
|  | AO |  | Spare | [6 empty] | MAIN 1 | 1 | 5
|  | Counter |  | MCA 1 Flow | MCA 1 | [5 empty] | MAIN 1 | 2 | 0
|  | Counter |  | MCA 2 Flow | MCA 2 | [5 empty] | MAIN 1 | 2 | 2
|  | Counter |  | MoldAC Flow | MOLD AC | [5 empty] | MAIN 1 | 2 | 4
|  | Counter |  | Spare | [6 empty] | MAIN 1 | 2 | 6
|  | DI |  | PowerFail2_In | Build ON SITE | [5 empty] | Remote 0 | 1 | 0
|  | DI |  | Treat2_OverPSIsw_In | [6 empty] | Remote 0 | 1 | 1
|  | DI |  | Treat2_AlmostFullsw_In | [6 empty] | Remote 0 | 1 | 2
|  | DI |  | Treat2_Fullsw_In | [6 empty] | Remote 0 | 1 | 3
|  | DI |  | Hydraulic Pump Run Status (NOT IN USE IN OLD PLC) | [6 empty] | Remote 0 | 1 | 4
|  | DI |  | Treat2_Door1LeverClosed_In | [6 empty] | Remote 0 | 1 | 5
|  | DI |  | Treat2_StripEmptysw_In | [6 empty] | Remote 0 | 1 | 6
|  | DI |  | Treat2_Liquidsw_In | [6 empty] | Remote 0 | 1 | 7
|  | DI |  | Pit 3 Level Control | [6 empty] | Remote 0 | 1 | 8
|  | DI |  | Spare | [6 empty] | Remote 0 | 1 | 9
|  | DI |  | Spare | [6 empty] | Remote 0 | 1 | 10
|  | DI |  | Pit 4 Level Control | [6 empty] | Remote 0 | 1 | 11
|  | DI |  | Spare | [6 empty] | Remote 0 | 1 | 12
|  | DI |  | WT4_Overflowsw_In | [6 empty] | Remote 0 | 1 | 13
|  | DI |  | WT5_Overflowsw_In | [6 empty] | Remote 0 | 1 | 14
|  | DI |  | Pit 2 Level Control | [6 empty] | Remote 0 | 1 | 15
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 0
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 1
|  | DI |  | Unloading Pump Flow Sw | [6 empty] | Remote 0 | 2 | 2
|  | DI |  | Hydraulic Pump Stop Sw 2 | [6 empty] | Remote 0 | 2 | 3
|  | DI |  | Hydraulic Pump Stop Sw 1 | [6 empty] | Remote 0 | 2 | 4
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 5
|  | DI |  | Wax_Overflowsw_In | [6 empty] | Remote 0 | 2 | 6
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 7
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 8
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 9
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 10
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 11
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 12
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 13
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 14
|  | DI |  | Spare | [6 empty] | Remote 0 | 2 | 15
|  | DO |  | Mix3pmp_Out | [6 empty] | Remote 0 | 3 | 0
|  | DO |  | Treat2_Presspmp1_Out | [6 empty] | Remote 0 | 3 | 1
|  | DO |  | Treat2_Presspmp2_Out | [6 empty] | Remote 0 | 3 | 2
|  | DO |  | Treat2_Transpmp1_Out | [6 empty] | Remote 0 | 3 | 3
|  | DO |  | Mix1_M9-4vlv_Out | [6 empty] | Remote 0 | 3 | 4
|  | DO |  | Treat2_Strippmp1_Out | [6 empty] | Remote 0 | 3 | 5
|  | DO |  | Treat2_Vacpmp1_Out | [6 empty] | Remote 0 | 3 | 6
|  | DO |  | Treat2_SealWaterpmp_Out | [6 empty] | Remote 0 | 3 | 7
|  | DO |  | Spare | [6 empty] | Remote 0 | 3 | 8
|  | DO |  | Spare | [6 empty] | Remote 0 | 3 | 9
|  | DO |  | UnloadingPadSumppmp_Out (DNE) | [6 empty] | Remote 0 | 3 | 10
|  | DO |  | Treat2_DoorpitSumppmp_Out | [6 empty] | Remote 0 | 3 | 11
|  | DO |  | Treat2_Doorpmp_Out | [6 empty] | Remote 0 | 3 | 12
|  | DO |  | Treat2_T1vlv_Out | [6 empty] | Remote 0 | 3 | 13
|  | DO |  | Treat2_T2vlv_Out | [6 empty] | Remote 0 | 3 | 14
|  | DO |  | Treat2_T3vlv_Out | [6 empty] | Remote 0 | 3 | 15
|  | DO |  | Treat2_T4vlv_Out | [6 empty] | Remote 0 | 4 | 0
|  | DO |  | Treat2_P1vlv_Out | [6 empty] | Remote 0 | 4 | 1
|  | DO |  | Treat2_P2vlv_Out | [6 empty] | Remote 0 | 4 | 2
|  | DO |  | Treat2_S1vlv_Out | [6 empty] | Remote 0 | 4 | 3
|  | DO |  | Treat2_S2vlv_Out | [6 empty] | Remote 0 | 4 | 4
|  | DO |  | Mix1_M19vlv_Out | [6 empty] | Remote 0 | 4 | 5
|  | DO |  | Mix1_M4-4Bvlv_Out | [6 empty] | Remote 0 | 4 | 6
|  | DO |  | Mix1_M1-4vlv_Out | [6 empty] | Remote 0 | 4 | 7
|  | DO |  | MD4vlv_Out | [6 empty] | Remote 0 | 4 | 8
|  | DO |  | MD5vlv_Out | [6 empty] | Remote 0 | 4 | 9
|  | DO |  | MS4vlv_Out | 4 1 | [5 empty] | Remote 0 | 4 | 10
|  | DO |  | MS5vlv_Out | 4 2 | [5 empty] | Remote 0 | 4 | 11
|  | DO |  | Treat2_V1vlv_Out | 4 3 | [5 empty] | Remote 0 | 4 | 12
|  | DO |  | Treat2_V2vlv_Out | 4 4 | [5 empty] | Remote 0 | 4 | 13
|  | DO |  | Treat2_C1vlv_Out | 5 1 | [5 empty] | Remote 0 | 4 | 14
|  | DO |  | SV4_vlv_Out | 5 2 | [5 empty] | Remote 0 | 4 | 15
5 3
|  | DO |  | SV5_vlv_Out | 5 4 | [5 empty] | Remote 0 | 5 | 0
|  | DO |  | Treat2_Tnkv4vlv_Out | [6 empty] | Remote 0 | 5 | 1
|  | DO |  | Treat2_Tnkv5vlv_Out | [6 empty] | Remote 0 | 5 | 2
|  | DO |  | Treat2_SealWatervlv1_Out | [6 empty] | Remote 0 | 5 | 3
|  | DO |  | Treat2_SealWatervlv2_Out | [6 empty] | Remote 0 | 5 | 4
|  | DO |  | Waxpmp_Out | [6 empty] | Remote 0 | 5 | 5
|  | DO |  | Mix4pmp_Out | [6 empty] | Remote 0 | 5 | 6
|  | DO |  | Mix1_M3-3vlv_Out | [6 empty] | Remote 0 | 5 | 7
|  | DO |  | Mix1_M2-3vlv_Out | [6 empty] | Remote 0 | 5 | 8
|  | DO |  | Treat2_R5vlv_Out | [6 empty] | Remote 0 | 5 | 9
|  | DO |  | Treat2_R4vlv_Out | [6 empty] | Remote 0 | 5 | 10
|  | DO |  | Spare | [6 empty] | Remote 0 | 5 | 11 | Old WRC Agitator
|  | DO |  | TankFarmSumppmp_Out | [6 empty] | Remote 0 | 5 | 12
|  | DO |  | Spare | [6 empty] | Remote 0 | 5 | 13
|  | DO |  | Spare | [6 empty] | Remote 0 | 5 | 14 | Old FldTreat2GreenLight
|  | DO |  | Treat2_Transpmp2_Out | [6 empty] | Remote 0 | 5 | 15
|  | DO |  | Spare | [6 empty] | Remote 0 | 6 | 0
|  | DO |  | MS6vlv_Out | [6 empty] | Remote 0 | 6 | 1
|  | DO |  | SV10_vlv_Out | [6 empty] | Remote 0 | 6 | 2
|  | DO |  | Spare | [6 empty] | Remote 0 | 6 | 3 | OLD PA Pump
|  | DO |  | Mix1_M2-4vlv_Out | [6 empty] | Remote 0 | 6 | 4
|  | DO |  | Spare | [6 empty] | Remote 0 | 6 | 5 | OLD MS17 Valve
|  | DO |  | Treat2_T6vlv_Out | [6 empty] | Remote 0 | 6 | 6
|  | DO |  | Treat2_T5vlv_Out | [6 empty] | Remote 0 | 6 | 7
|  | DO |  | Mix1_M4-3Bvlv_Out | [6 empty] | Remote 0 | 6 | 8
|  | DO |  | MD6vlv_Out | [6 empty] | Remote 0 | 6 | 9
|  | DO |  | Treat2_S3vlv_Out | [6 empty] | Remote 0 | 6 | 10
|  | DO |  | Spare | [6 empty] | Remote 0 | 6 | 11
|  | DO |  | Mix1_M8-4vlv_Out | [6 empty] | Remote 0 | 6 | 12
|  | DO |  | Treat2_T7vlv_Out | [6 empty] | Remote 0 | 6 | 13
|  | DO |  | SV9_vlv_Out (SV8 When output off) | [6 empty] | Remote 0 | 6 | 14
|  | DO |  | Treat2_F1vlv_Out (DNE) | [6 empty] | Remote 0 | 6 | 15
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 0
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 1
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 2
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 3
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 4
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 5
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 6
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 7
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 8
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 9
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 10
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 11
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 12
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 13
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 14
|  | DO |  | Spare | [6 empty] | Remote 0 | 7 | 15
|  | AI |  | Treat2 PSI | [6 empty] | Remote 1 | 1 | 0
|  | AI |  | WT4 Level | [6 empty] | Remote 1 | 1 | 1
|  | AI |  | WT5 Level | [6 empty] | Remote 1 | 1 | 2
|  | AI |  | OLD Process Tank | [6 empty] | Remote 1 | 1 | 3
|  | AI |  | WAX Level | [6 empty] | Remote 1 | 1 | 4
|  | AI |  | Spare | [6 empty] | Remote 1 | 1 | 5
|  | AI |  | Spare | [6 empty] | Remote 1 | 1 | 6
|  | AI |  | Spare | [6 empty] | Remote 1 | 1 | 7
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 0
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 1
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 2
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 3
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 4
|  | AI |  | Spare | [6 empty] | Remote 1 | 2 | 5
|  | AO |  | Treat2 Control Valve | [6 empty] | Remote 1 | 2 | 6
|  | AO |  | Spare | [6 empty] | Remote 1 | 2 | 7
|  | Counter |  | Nani Flow (DNE) | [6 empty] | Remote 1 | 3 | 0
|  | Counter |  | Unknown | [6 empty] | Remote 1 | 3 | 2
|  | Counter |  | CWM Flow | [6 empty] | Remote 1 | 3 | 4
|  | Counter |  | Unknown | [6 empty] | Remote 1 | 3 | 6
|  | Counter |  | WAX Flow | [6 empty] | Remote 1 | 4 | 0
|  | Counter |  | Spare | [6 empty] | Remote 1 | 4 | 2
|  | Counter |  | Spare | [6 empty] | Remote 1 | 4 | 4
|  | Counter |  | Spare | [6 empty] | Remote 1 | 4 | 6
|  | DO |  | Treat1_Presspmp1_Out | [6 empty] | ETH | - | - | 192.168.254.35
|  | DO |  | Treat1_Presspmp2_Out | [6 empty] | ETH | - | - | 192.168.254.36
|  | AO |  | Treat1_Presspmp1_Speed | [6 empty] | ETH | - | - | 192.168.254.35
|  | AO |  | Treat1_Presspmp2_Speed | [6 empty] | ETH | - | - | 192.168.254.36
|  | DO |  | Treat1_P2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S1
|  | DO |  | Treat1_P1vlv_Out | [6 empty] | VALVE PANEL 1 | - | S2
|  | DO |  | Treat1_P4vlv_Out | [6 empty] | VALVE PANEL 1 | - | S3
|  | DO |  | Treat1_P3vlv_Out | [6 empty] | VALVE PANEL 1 | - | S4
|  | DO |  | Treat1_T3vlv_Out | [6 empty] | VALVE PANEL 1 | - | S5
|  | DO |  | Treat1_T2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S6
|  | DO |  | Treat1_T1vlv_Out | [6 empty] | VALVE PANEL 1 | - | S7
|  | DO |  | Treat1_T4vlv_Out | [6 empty] | VALVE PANEL 1 | - | S8
|  | DO |  | Treat1_S1vlv_Out | [6 empty] | VALVE PANEL 1 | - | S9
|  | DO |  | Treat1_S2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S10
|  | DO |  | Treat1_T5vlv_Out | [6 empty] | VALVE PANEL 1 | - | S11
|  | DO |  | Mix1_M2-2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S12
|  | DO |  | Mix1_M7-2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S13
|  | DO |  | Mix1_M5-2vlv_Out (DNE) | [6 empty] | VALVE PANEL 1 | - | S14
|  | DO |  | Mix1_M4-2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S15
|  | DO |  | Mix1_M3-2vlv_Out | [6 empty] | VALVE PANEL 1 | - | S16
|  | DO |  | Treat1_R1vlv_Out | [6 empty] | VALVE PANEL 2 | - | S1
|  | DO |  | MD1vlv_Out | [6 empty] | VALVE PANEL 2 | - | S2
|  | DO |  | MS1vlv_Out | [6 empty] | VALVE PANEL 2 | - | S3
|  | DO |  | Treat1_TnkV1vlv_Out | [6 empty] | VALVE PANEL 2 | - | S4
|  | DO |  | Treat1_R2vlv_Out | [6 empty] | VALVE PANEL 2 | - | S5
|  | DO |  | MD2vlv_Out | [6 empty] | VALVE PANEL 2 | - | S6
|  | DO |  | MS2vlv_Out | [6 empty] | VALVE PANEL 2 | - | S7
|  | DO |  | Treat1_TnkV2vlv_Out | [6 empty] | VALVE PANEL 2 | - | S8
|  | DO |  | Treat1_R3vlv_Out | [6 empty] | VALVE PANEL 2 | - | S9
|  | DO |  | MD3vlv_Out | [6 empty] | VALVE PANEL 2 | - | S10
|  | DO |  | MS3vlv_Out | [6 empty] | VALVE PANEL 2 | - | S11
|  | DO |  | Treat1_TnkV3vlv_Out | [6 empty] | VALVE PANEL 2 | - | S12
|  | DO |  | Water1vlv_Out | [6 empty] | VALVE PANEL 2 | - | S13
|  | DO |  | Water2vlv_Out (DNE) | [6 empty] | VALVE PANEL 2 | - | S14
|  | DO |  | Mix1_M11vlv_Out | [6 empty] | VALVE PANEL 2 | - | S15
|  | DO |  | Spare | [6 empty] | VALVE PANEL 2 | - | S16

## Database Sign Off
DATABASE SIGN-OFF
| UFP SIGNOFF | TAS SIGNOFF | SIGNOFF DATE | COMMENTS
Table: Material
Field Names
PlantNumber
ChargeID
ItemNumber
ItemCode
ItemDesc
LocationCode
Depth
Width
Length
PackSize
Pieces
BoardFt
CubicFt
SquareFt
Grade
Type
Species
Mill
Standard
Retreat
RetreatCharge
Table: QC_Data
Field Names
ChargeNumber
Cylinder
Tank
PresAssay
PresRedrill
PresFinal
PresPenetration_Sampled
PresPenetration_Failed
BioAssay
BioRedrill
BioFinal
BioPenetration_Sampled
BioPenetration_Failed
PassFail
PreTotal
BioTotal
RedrillTotal
PenSampledTotal
PenFailedTotal
SolStart1
SolStart2
SolStart3
SolStart4
SolStart5
SolStart6
SolStart7
SolFinish1
SolFinish2
SolFinish3
SolFinish4
SolFinish5
SolFinish6
SolFinish7
TotalLbsGauge1
TotalLbsGauge2
TotalLbsGauge3
TotalLbsGauge4
TotalLbsGauge5
TotalLbsGauge6
TotalLbsGauge7
TotalLbsAdj1
TotalLbsAdj2
TotalLbsAdj3
TotalLbsAdj4
TotalLbsAdj5
TotalLbsAdj6
TotalLbsAdj7
RetAdj1
RetAdj2
RetAdj3
RetAdj4
RetAdj5
RetAdj6
RetAdj7
StripFactor1
StripFactor2
StripFactor3
StripFactor4
StripFactor5
StripFactor6
StripFactor7
QCOperator
ChangeReason
Result
PresQCFactor
BioQCFactor
RawBioAssay
RawRedrillPresAssay
RawRedrillBioAssay

## Tank And Chem Number
ALL TANKS |  | MIX System 1
Tank NO. | Description | Chem NO. | Description | Card | Channel | K Factor | Unit from SCADA(0= Gal, 1 =Oz)
1 | WORKTANK 1 | 1 | Water | 0 | 0 | 1 | 0
2 | WORKTANK 2 | 2 | MCA | 9 | 2 | 100
3 | WORKTANK 3 | 3 | Mold Ac | 10 | 0 | 55
4 | WORKTANK 4 | 4
5 | WORKTANK 5 | 5 | HE45 | 9 | 0 | 53
6 | WORKTANK 6 | 6 | Wax | 10 | 6 | 100
7 | WORKTANK 7 | 7 |  | 10 | 2 | 100
8 | WORKTANK 8 | 8
9 | WORKTANK 9 | 9
10 | WORKTANK 10 | 10
11 | Water 1 | 11
12 | MCA | 12
13 | Mold Ac | 13
14 | NANI | 14
15 | CWM | 15
16 |  | 16
17
18
19 | Water 2
20 | Wax |  |  | Need to UPDATED
21 | Eco 2 (Right)
22 | Borate Mix
23 | CAC
24
25
26
27
28

## Network Schema
Device | Model (If applicable) | IP Address | Subnet | Gateway | Node | Notes | Admin User Login | Admin User Password | Noteable Registers
Schneider PLC NOE 1
Main PLC
Tram PLC